## Slide 1
PES GOLD Panel Session
IEEE PES GM July 22, 2013 – Vancouver, Canada
Dr. Rafael Segundo
KTH SmarTS Lab (rafael.segundo@kth.se)
Prof. Luigi Vanfretti
KTH SmarTS Lab (luigiv@kth.se), Statnett SF (luigi.vanfretti@statnett.no)
Offline Impact Assessment of Dynamic Simulations in the
EU FP7-funded iTesla Project

## Slide 2: Project description
A EU-funded FP7 project coordinated by RTE
  7 transmission network operators (RTE, Statnett, National Grid, Elia, REN, Coreso, IPTO), 7 SMES, 3 R&D centers and 3 Universities (KTH, Imperial College and KULeuven)
  4 years of duration, 13.2 M€
Main objective: to develop a toolbox for use of TSOs to operate the European power system in the years to come
  To validate the toolbox at the pan-European level
  The toolbox will allow to assess the (dynamic) security of the power system from 2-days ahead to real-time and provide preventive or curative actions when needed
Considers six large challenges – two of which are:
  To take into account system dynamics in security assessment
  To take into account large networks with a need for coordination

## Slide 3: Overview of iTesla
The iTesla toolbox addresses :
  Decision making under uncertainties,
  New flexibility brought by corrective actions,
  Dynamic modeling and simulations.
With the help of:
  High performance computing,
  Data mining techniques.
  Will be a major improvement in security assessment tools.

## Slide 4: Indices for Impact Assessment
The impact assessment is part of the offline analysis aim to provide criteria to the online analysis.
Following a dynamic simulation for a specific contingency, the output data is used to calculate a set of severity indices. These indices, should measure the quality of the stability or severity of the instability.
The indexes will indicate:
If the system will converge to a safe and stable equilibrium point.
To indicate the severity of the instability/stability for each type instability mechanism
Static concerns |  | Dynamic concerns | 
1. Post-fault overloads of lines | 2. Post-fault bus under- or over-voltages | 3. Small-signal stability | 4. Transient stability

## Slide 5: 1. Post-fault Overloads Index
Indicate if the post-fault line flows exceed the network capacity by observing the power flows through the transmission lines after an outage occurs.
post-fault flow trough transmission line k
(from dynamic simulation)
Capacity of transmission line k (from network data)
Weighting factor
i.e. wfk=[1,1,…,1] for a uniform weight
The index is not a simple summation, it is in fact a norm (or pseudo-norm if m<1): the term wfk can be used to weight and give more importance to specific lines.
Index Classification
Parameter (from choosing a m-norm)

## Slide 6: Overloads: Case study 1
Case study: 898 lines, disturbance at 2sec
Analyzed window

## Slide 7
Criteria: Smean should not exceed more than 10%, the nominal value
Only 3 lines with slight violation of the limits
3.84%
0.8%
7.28%
Lines violating Smax value
Snom=5.69
Smax=6.26
Smean=6.72
Note that this index is based on the average value

## Slide 8: Overloads: Case study 2
Case study: 118 lines, sever disturbance at 10 sec.
Analyzed window

## Slide 9
43 lines violating the limits
Criteria: Smean should not exceed more than 10%, the nominal value
Snom=19.3
Smean=195.5
Smax=21.26

## Slide 10: 2. Post-fault Under-/Over-Voltage Index
Indicates whether or not the bus voltages deviations exceed those acceptable in the grid code, by observing the voltage across the transmission network after a contingency has occurred.
Bus voltage magnitudes
(from dynamic simulation)
maximum acceptable voltage deviation (from the network data)
Rated voltage
(from network data)
The index is not a simple summation and we can use weights vx,k to give more importance to specific nodes.
Weighting factor
i.e. wvk=[1,1,…,1] for a uniform weight
Parameter (from choosing a q-norm)
Index Classification

## Slide 11: Under/over Voltage: Case study 1
Case study: 50 buses, disturbance at 10sec
Analyzed window

## Slide 12
Only 5 buses with slight violation of the limits
Note that this index is based on the average value.

## Slide 13
Case study: 6799 buses, severe disturbance at 62 sec.
Under/over Voltage: Case study 2

## Slide 14
15975 buses violating the limits

## Slide 15: 3. Small-signal Stability Index
In this index the eigenvalues of the system from the dynamic simulation sequence are estimated using appropriate signal processing techniques.
A measure of the stability of the system will be the damping ratio of the system, where the requirement of a stable case could be set to a damping ratio of for example 5%.
Signal processing
for eigenvalues estimation

## Slide 16: Small-signal Case study
Case study: 6799 buses, disturbance at 2 sec.
Signals with highest oscillatory content

## Slide 17
One inter-area mode (0.66Hz) identified with ζ=1% damping ratio
Simulation classified as unstable
(minimum ζ=5% )
Signal Processing and eigenvalue estimation

## Slide 18: 4. Transient stability (rotor-angle stability)
To evaluate the transient stability of the system, a simple approach that looks at the angular deviation from the center of inertia angle has ben chosen. In this way we can see if any uncontrolled inter-area oscillations (loss of synchronism) exist. The multimachine integral square generator angle index (ISGA) is used.
Machines inertias (2 *H)
Generator angles
Center of angle (COA)

## Slide 19: Transient Stability: case study 1
Case study: 772 machines, different disturbances at 2, 22, 42 and 62 sec, total simulation length of 82 sec.
Analyzing TS after disturbance at 2 sec

## Slide 20
31.9954
No transient stability
Note that might be required to normalize this index

## Slide 21: Transient Stability: case study 2
Case study: 772 machines, disturbances at 2, 22, 42 and 62 sec, total simulation length of 82 sec.
Analyzing TS after last disturbance at 62 sec

## Slide 22
2.7852e+005
Severe transient stability problem

## Slide 23: Main Challenges
Related to integration of the proposed algorithms:
  Interaction and information exchange among the different partners
  The indices validated using dynamic simulations from our different partners.
  Large amount of information to analyze
  Integrate the final algorithms with all of the partners
Computational challenges:
  Automation of index computations
Severity index capability to forecast:
  An actual stability condition in the grid (… are the models good enough?)
  Capability to discern the originating instability failure mode (e.g. small signal, voltage…) in grid collapse scenarios where different (or all) types of instability are involved

## Slide 24: THANKS! QUESTIONS?