## Slide 1: WP4.3
Rafael Segundo and Luigi Vanfretti – KTH
June 25th, 2013, Nice, France

## Slide 2: Introduction
In this presentation it is shown part of the validation of the different indices. Illustrative examples using real data provided by WP4.3 partners are presented.
Organization of the presentation:
Information received
Under/over voltage
  Case studies
Overloads
  Case studies
Transient Stability
  Case studies
Future work

## Slide 3: Signal Classification
Pre-contingency
Post-contingency
Nonlinear
behavior
Window to be analyzed
It is necessary to classify each of the signals into different parts before to be analyzed:
Pre-contingency: period of time where the signal is in nominal conditions (no disturbance).
Post-contingency: Period of time just after any disturbance in the system.
Nonlinear behavior: Short period of time, few seconds, after a disturbance.
Window to be analyzed: Small window of time before the end of the simulation and after any contingency and the nonlinear behavior.

## Slide 4: Post-fault under/over voltage
Useful to observer whether the deviation of voltages surpass those acceptable in the operational standards. Monitoring the voltage across the transmission network right after an outage occurs.
Considerations
Total index of all the buses
Number of buses
Individual index of bus k
Nominal voltage at bus k
Voltages of bus k in the selected window
Maximum voltage at bus k
Minimum voltage at bus k
Weighting factor of line k
Exponent to make violations values evident
Index Classification

## Slide 5: Under/over Voltage: Case study 1
Case study: 6799 buses, disturbance at 2sec, simulation length 20 sec .
Analyzed window

## Slide 6
Only 5 buses with slight violation of the limits
Note that this index is based on the maximum point of the analyzed window, another option is to consider the average value

## Slide 7
Case study: 6799 buses, severe disturbance at 62 sec.
Under/over Voltage: Case study 2

## Slide 8
15975 buses violating the limits

## Slide 9: Post-fault overloads
Considerations
Total index
Number of lines
Individual index of line ”k”
Mean value of line ”k”
Maximum power allowed in line ”k”
weighting factor of line ”k”
Exponent to make violations values evident
Index Classification
Useful to observer if the post-fault flows surpass the network capacity. Monitoring the power flows through the transmission lines right after an outage occurs.

## Slide 10: Overloads: Case study 1
Case study: 898 lines, disturbance at 2sec, simulation length 20 sec .
Analyzed window

## Slide 11
Only 3 lines with slight violation of the limits
3.84%
0.8%
7.28%
Criteria: Smean should not exceed more than 10%, the nominal value
Lines violating Smax value
Snom=5.69
Smax=6.26
Smean=6.72
Note that this index is based on the average value

## Slide 12: Under/over Voltage: Case study 2
Case study: 118 lines, sever disturbance at 10 sec, simulation length of 15 sec.
Analyzed window

## Slide 13
43 lines violating the limits
Criteria: Smean should not exceed more than 10%, the nominal value
Snom=19.3
Smean=195.5
Smax=21.26

## Slide 14: Transient stability
Multimachine integral square generator angle index (ISGA).
Considerations
Disconnected generator are not included in the summation of Mt
Total index ISGA
Total machine inertia
Individual machine inertia
Number of simulation seconds
Number of Machines
Rotor angle of machine “i”
Center of angle
Index Classification
Value that depend of different factors such as: number of machines, inertia of the machines.

## Slide 15: Illustrative example
0.1837 +0.3674= 0.5511
Two machines:
Inertia of Machie 2 is two times the Inertia of Machie 1
The total index is the integral of the distance from each machine to the center of inertia or angle.

## Slide 16: Transient Stability: case study 1
Case study: 772 machines, different disturbances at 2, 22, 42 and 62 sec, total simulation length of 82 sec.
Analyzing TS after disturbance at 2 sec

## Slide 17
31.9954
No transient stability
Note that might be required to normalize this index

## Slide 18: Transient Stability: case study 2
Case study: 772 machines, disturbances at 2, 22, 42 and 62 sec, total simulation length of 82 sec.
Analyzing TS after last disturbance at 62 sec

## Slide 19
2.7852e+005
Severe transient stability problem

## Slide 20: Conclusions
Over/under voltage index can be calculated based on the maximum violation point or in the average value.
Limits for voltage and overload has been considered as a given plus\minus percent.
Transient stability index might need to be normalized
More simulations to validate voltage stability index will be provided by RTE